## Slide 1: Encore-flexible Heatpump
May 2022
Shahla Huseynova

## Slide 2
Sensible heat storage
Water storage-input parameters
Water storage as a flexibility to heat pump to increase the source temperature and thus COP
Efficiency = 100 % for now
Max, min power
Capacity per volume = 50 * 1e-3 MWh/m3
Volume = 1000 m3
Max storage capacity = 50 MWh
Lifetime = 25 years
Temperature = 368 K (95C)
Min storage level = 5 MWh
Max storage level = 0.95* Max storage capacity

## Slide 3
Encore
First approach
Evaporator
Compressor
Exp. valve
Condenser
Water storage
Water source
COP
HP sink temp =80-170
HP source T
Factory
25-75 0C

## Slide 4
Encore
Coil option
Evaporator
Compressor
Exp. valve
Condenser
Water
storage
Water source
COP
HP sink temp =80-170
HP source T
Factory
25-75 0C

## Slide 5
Evaporator
Compressor
Exp. valve
Condenser
Water
storage
Water source
COP
HP sink temp =80-170
Factory
25-75 0C
Outlet is HP source, inlet flow is HP sink?
Encore
Condenser side

## Slide 6
Evaporator
Compressor
Exp. valve
Condenser
COP
Process
Idea Recoy: use thermal storage to increase temperature of waste heat stream that goes into evaporator
Process Waste Heat
25-75 0C
Source water
To ambient or return to process
Thermal storage
Hot water
Return water
Modification RDB
-Hot water circuit feeds
in a closed loop into
the storage. A pump in the hot water circuit can control the flow on that side

## Slide 7
Encore
Evaporator
Compressor
Exp. valve
Condenser
Thermal
storage
COP
Process
Idea Recoy: use thermal storage to increase temperature of waste heat stream that goes into evaporator
Process Waste Heat
25-75 0C
Source water
To ambient or return to process
Modification RDB
-Hot water circuit feeds
in a closed loop into
the storage. A pump in the hot water circuit can control the flow on that side . Now Equal to slide 1
Fresh water

## Slide 8
Encore
With stratified tank
Evaporator
Compressor
Exp. valve
Condenser
Thermal
storage
55
COP
Process
Idea Recoy: use thermal storage to increase temperature of waste heat stream that goes into evaporator
Process Waste Heat
25-75
Feed water
15 C
To ambient or return to process
Tsink=125-170
T=Tsink
MW=X
MW=Y-X
MW=Y (max heat output)
T=Tsink
95
95
Fresh water

## Slide 9
Encore
Process flow and modelling approach combined
Evaporator
Compressor
Exp. valve
Condenser
Thermal
storage
55
COP
Process
Process Waste Heat
25-75
To ambient or return to process
Tsink=125-170
T=Tsink
MW=X
MW=Y-X
MW=Y (max heat output)
T=Tsink
95
95
Fresh water

## Slide 10
Encore
Simplification for the Modeling approach
Heat pump
Process
Storage
31MW
140 C
MW
60 C
42 kg/s
52kg/s
42 kg/s
10 kg/s
140 C
6 MW
95C
6 MW
140C
13 kg/s
1
2
3
4
5
6
13*95 + 60*42= (13+42)*T
T=68

## Slide 11
Encore
New Tsource and COP calculation
Q= ṁ - )
Tref is assumed to be 0 C.
Temperatures will be converted to K.
Cp is assumed to be the same in all flow streams
Heat loss is neglected, assumed to have perfect-insulation
= + (By knowing hp capacity, demand and Tsink, was found
= + (by energy balance around storage with a 100 % efficiency and 95 C of heat provided from storage, is calculated)
From -) + -) = -) , Tsource new is calculated and subsequently new COP can be calculated

## Slide 12
Encore
Steps for heat pump and storage interaction
1. Follows this heuristic logic based on given price:
- If electricity price is low --> Heatpump at full power, and charge the storage
- If electricity price is low --> Tsource is lower than the median temperature, discharge the storage??
- If electricity price is high --> Discharge the heat storage, and increase Tsource, which will increase COP
2. Cost calculation of heat production
- Costs are based on electricity consumption of heat pump
- Energy is procured in day-ahead market, assuming that heat pump runs baseload without heat storage
- Electricity cons. for the new system with storage is calculated in the simulation case.
- Imbalance volumes are calculated per 15 mins
- This imbalance volume is charged on the imbalance market (POS price if consumed less, NEG price if consumed more)

## Slide 13
Encore
Storage functions in the model
Water storage is charged to its maximum storage level
Water storage is discharged until minimum storage level.
Storage level is set to new level after charging/discharging or stand-by case.
Volume can be optimized
Storage Capex: 10 Euro/kWh

## Slide 14
Encore
Imbalance prices vs day-ahead prices
November 2018 electricity prices

## Slide 15
Dynamics of the model
The results of 2 days

## Slide 16
Dynamics of the model
When the storage is discharged, COP increase
To storage power also aligns with the storage level
Total saving is 2.3% per month

## Slide 17
Encore
Appendix

## Slide 18
Heat Storage
Vergelijking met andere energie opslag technologieën
(World Energy Council, 2016)

## Slide 19
Heat Storage
Storage duration vs. Cost
The longer the storage period, the lower the investment costs (€ / kWh) must be to make it economically interesting

## Slide 20
Heat Storage
Comparison heat storage technologies
(IEA-ETSAP & ARENA, 2012)